## ReadMe
IES GenAI for Engineers | v2.0 ¦ Three-lab Excel workshop
Status | IES ¦ Original synthetic CW-401 engineering case. Values and limits are fictional teaching assumptions, not plant operating instructions. Generated references are independently calculated examples, not recorded Copilot executions.
How to use | Save a working copy of Starter.xlsx to your approved OneDrive or SharePoint location. Open it in Excel with your work/school account and use the Copilot side pane. Select the named table before prompting. If Copilot cannot edit, request the formula and insert it manually; record the fallback. Confirm tenant entitlement and supported workbook format before class. Keep the local raw files unchanged.
Workbook prompts | Trainer-authored prompts in Prompts. The previously mentioned external Excel prompt file has not been supplied; these are not attributed to that file.
Case | industrial cooling-water utility uses duty/standby metering pumps DP-401A/B. The workshop CTQ is measured delivery during a standardised collection test at fixed commanded setting. The design-note teaching target is 62.0 L/h with an acceptance band of 58.9–65.1 L/h; this is a delivery-test specification, not a chemical dose or water-quality compliance limit. Chemical identity and operating procedures are deliberately outside the case. A repeatability study and comparison of pump delivery are needed before a maintenance recommendation. The team has 60 baseline collection tests, 30 subsequent monitoring tests and 30 post-intervention pilot tests. Collection volume is measured over 120 seconds; delivery L/h = collected litres × 30. The command setting is fixed for comparability; shift and pump identity are retained to detect confounding. The monitoring period includes a sustained delivery reduction coinciding with a differential-pressure increase. A work order records inspection and a strainer replacement before the pilot. This temporal association does not isolate root cause: the pilot also follows a verification check, so intervention effects are confounded. No randomised causal claim is justified.
Worked reference | Illustrative formulas and charts, independently computed; not an actual Copilot session.

## RawTests
test_id | timestamp_SGT | phase | shift | pump_tag | flow_instrument | collection_vessel | commanded_L_h | collected_L | duration_s | strainer_dp_bar | ambient_C | quality_flag | calibration_record
TEST-001 | 2026-08-03T07:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.052 | 120 | 0.216 | 28.2 | VALID | CAL-401-08
TEST-002 | 2026-08-03T11:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.051 | 120 | 0.167 | 28.3 | VALID | CAL-401-08
TEST-003 | 2026-08-03T15:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.066 | 120 | 0.199 | 27.6 | VALID | CAL-401-08
TEST-004 | 2026-08-03T19:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.104 | 120 | 0.191 | 26.8 | VALID | CAL-401-08
TEST-005 | 2026-08-03T23:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.059 | 120 | 0.194 | 27.2 | VALID | CAL-401-08
TEST-006 | 2026-08-04T03:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.069 | 120 | 0.149 | 27.5 | VALID | CAL-401-08
TEST-007 | 2026-08-04T07:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.038 | 120 | 0.162 | 26.3 | VALID | CAL-401-08
TEST-008 | 2026-08-04T11:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.045 | 120 | 0.165 | 28.2 | VALID | CAL-401-08
TEST-009 | 2026-08-04T15:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.06 | 120 | 0.199 | 28.9 | VALID | CAL-401-08
TEST-010 | 2026-08-04T19:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.079 | 120 | 0.158 | 27.7 | VALID | CAL-401-08
TEST-011 | 2026-08-04T23:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.092 | 120 | 0.186 | 30.4 | VALID | CAL-401-08
TEST-012 | 2026-08-05T03:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.067 | 120 | 0.157 | 27.7 | VALID | CAL-401-08
TEST-013 | 2026-08-05T07:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.089 | 120 | 0.173 | 26.9 | VALID | CAL-401-08
TEST-014 | 2026-08-05T11:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.058 | 120 | 0.194 | 26.2 | VALID | CAL-401-08
TEST-015 | 2026-08-05T15:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.094 | 120 | 0.203 | 27.5 | VALID | CAL-401-08
TEST-016 | 2026-08-05T19:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.069 | 120 | 0.207 | 27.1 | VALID | CAL-401-08
TEST-017 | 2026-08-05T23:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.058 | 120 | 0.144 | 27.4 | VALID | CAL-401-08
TEST-018 | 2026-08-06T03:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.088 | 120 | 0.173 | 26.8 | VALID | CAL-401-08
TEST-019 | 2026-08-06T07:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.098 | 120 | 0.185 | 26.6 | VALID | CAL-401-08
TEST-020 | 2026-08-06T11:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.054 | 120 | 0.186 | 29.3 | VALID | CAL-401-08
TEST-021 | 2026-08-06T15:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.039 | 120 | 0.189 | 28.9 | VALID | CAL-401-08
TEST-022 | 2026-08-06T19:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.052 | 120 | 0.193 | 26.6 | VALID | CAL-401-08
TEST-023 | 2026-08-06T23:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.101 | 120 | 0.188 | 29 | VALID | CAL-401-08
TEST-024 | 2026-08-07T03:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.067 | 120 | 0.169 | 27.4 | VALID | CAL-401-08
TEST-025 | 2026-08-07T07:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.105 | 120 | 0.18 | 28.1 | VALID | CAL-401-08
TEST-026 | 2026-08-07T11:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.072 | 120 | 0.165 | 28.2 | VALID | CAL-401-08
TEST-027 | 2026-08-07T15:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.049 | 120 | 0.19 | 27.8 | VALID | CAL-401-08
TEST-028 | 2026-08-07T19:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.077 | 120 | 0.173 | 27.2 | VALID | CAL-401-08
TEST-029 | 2026-08-07T23:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.062 | 120 | 0.169 | 28.3 | VALID | CAL-401-08
TEST-030 | 2026-08-08T03:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.043 | 120 | 0.183 | 28.8 | VALID | CAL-401-08
TEST-031 | 2026-08-08T07:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.066 | 120 | 0.148 | 27.8 | VALID | CAL-401-08
TEST-032 | 2026-08-08T11:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.084 | 120 | 0.195 | 29.1 | VALID | CAL-401-08
TEST-033 | 2026-08-08T15:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.052 | 120 | 0.153 | 30.2 | VALID | CAL-401-08
TEST-034 | 2026-08-08T19:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.067 | 120 | 0.178 | 29 | VALID | CAL-401-08
TEST-035 | 2026-08-08T23:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.037 | 120 | 0.17 | 27.1 | VALID | CAL-401-08
TEST-036 | 2026-08-09T03:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.065 | 120 | 0.151 | 30.1 | VALID | CAL-401-08
TEST-037 | 2026-08-09T07:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.069 | 120 | 0.195 | 28.3 | VALID | CAL-401-08
TEST-038 | 2026-08-09T11:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.074 | 120 | 0.191 | 28.4 | VALID | CAL-401-08
TEST-039 | 2026-08-09T15:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.056 | 120 | 0.202 | 29.4 | VALID | CAL-401-08
TEST-040 | 2026-08-09T19:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.076 | 120 | 0.208 | 30.1 | VALID | CAL-401-08
TEST-041 | 2026-08-09T23:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.037 | 120 | 0.203 | 27.2 | VALID | CAL-401-08
TEST-042 | 2026-08-10T03:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.052 | 120 | 0.149 | 27.8 | VALID | CAL-401-08
TEST-043 | 2026-08-10T07:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.065 | 120 | 0.185 | 28.4 | VALID | CAL-401-08
TEST-044 | 2026-08-10T11:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.038 | 120 | 0.198 | 29.3 | VALID | CAL-401-08
TEST-045 | 2026-08-10T15:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.077 | 120 | 0.173 | 27.5 | VALID | CAL-401-08
TEST-046 | 2026-08-10T19:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.101 | 120 | 0.189 | 26.1 | VALID | CAL-401-08
TEST-047 | 2026-08-10T23:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.043 | 120 | 0.189 | 27.7 | VALID | CAL-401-08
TEST-048 | 2026-08-11T03:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.082 | 120 | 0.152 | 28.3 | VALID | CAL-401-08
TEST-049 | 2026-08-11T07:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.083 | 120 | 0.18 | 27.8 | VALID | CAL-401-08
TEST-050 | 2026-08-11T11:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.058 | 120 | 0.221 | 26.2 | VALID | CAL-401-08
TEST-051 | 2026-08-11T15:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.102 | 120 | 0.157 | 28.5 | VALID | CAL-401-08
TEST-052 | 2026-08-11T19:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.077 | 120 | 0.189 | 28.6 | VALID | CAL-401-08
TEST-053 | 2026-08-11T23:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.051 | 120 | 0.172 | 29.1 | VALID | CAL-401-08
TEST-054 | 2026-08-12T03:00:00+08:00 | baseline | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.03 | 120 | 0.18 | 28.5 | VALID | CAL-401-08
TEST-055 | 2026-08-12T07:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.056 | 120 | 0.157 | 27.9 | VALID | CAL-401-08
TEST-056 | 2026-08-12T11:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.063 | 120 | 0.19 | 28.9 | VALID | CAL-401-08
TEST-057 | 2026-08-12T15:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.019 | 120 | 0.178 | 26 | VALID | CAL-401-08
TEST-058 | 2026-08-12T19:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.097 | 120 | 0.162 | 28.9 | VALID | CAL-401-08
TEST-059 | 2026-08-12T23:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.088 | 120 | 0.181 | 29 | VALID | CAL-401-08
TEST-060 | 2026-08-13T03:00:00+08:00 | baseline | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.083 | 120 | 0.189 | 28.5 | VALID | CAL-401-08
TEST-061 | 2026-08-13T07:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.084 | 120 | 0.188 | 29.1 | VALID | CAL-401-08
TEST-062 | 2026-08-13T11:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.051 | 120 | 0.183 | 29.2 | VALID | CAL-401-08
TEST-063 | 2026-08-13T15:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.032 | 120 | 0.196 | 28.3 | VALID | CAL-401-08
TEST-064 | 2026-08-13T19:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.039 | 120 | 0.196 | 27.5 | VALID | CAL-401-08
TEST-065 | 2026-08-13T23:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.066 | 120 | 0.201 | 29.3 | VALID | CAL-401-08
TEST-066 | 2026-08-14T03:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.058 | 120 | 0.202 | 26.2 | VALID | CAL-401-08
TEST-067 | 2026-08-14T07:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.077 | 120 | 0.177 | 29.9 | VALID | CAL-401-08
TEST-068 | 2026-08-14T11:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 |  | 120 | 0.155 | 27 | MISSING_VOLUME | CAL-401-08
TEST-069 | 2026-08-14T15:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.05 | 120 | 0.189 | 27.7 | VALID | CAL-401-08
TEST-070 | 2026-08-14T19:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.032 | 120 | 0.163 | 27.4 | VALID | CAL-401-08
TEST-071 | 2026-08-14T23:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.104 | 120 | 0.188 | 28.1 | VALID | CAL-401-08
TEST-072 | 2026-08-15T03:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.07 | 120 | 0.21 | 27.9 | VALID | CAL-401-08
TEST-073 | 2026-08-15T07:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.929 | 120 | 0.434 | 27.6 | VALID | CAL-401-08
TEST-074 | 2026-08-15T11:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.97 | 120 | 0.389 | 28.9 | VALID | CAL-401-08
TEST-075 | 2026-08-15T15:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.915 | 120 | 0.417 | 26.4 | VALID | CAL-401-08
TEST-076 | 2026-08-15T19:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.927 | 120 | 0.398 | 27.9 | VALID | CAL-401-08
TEST-077 | 2026-08-15T23:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.907 | 120 | 0.425 | 26.6 | VALID | CAL-401-08
TEST-078 | 2026-08-16T03:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.977 | 120 | 0.431 | 28 | VALID | CAL-401-08
TEST-079 | 2026-08-16T07:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 1.936 | 120 | 0.431 | 27.5 | VALID | CAL-401-08
TEST-080 | 2026-08-16T11:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 1.904 | 120 | 0.422 | 29.5 | VALID | CAL-401-08
TEST-081 | 2026-08-16T15:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 1.942 | 120 | 0.427 | 27.6 | VALID | CAL-401-08
TEST-082 | 2026-08-16T19:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 1.937 | 120 | 0.424 | 28.4 | VALID | CAL-401-08
TEST-083 | 2026-08-16T23:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 1.948 | 110 | 0.41 | 28 | INVALID_DURATION | CAL-401-08
TEST-084 | 2026-08-17T03:00:00+08:00 | monitoring | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 1.929 | 120 | 0.427 | 29 | VALID | CAL-401-08
TEST-085 | 2026-08-17T07:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.943 | 120 | 0.404 | 28.5 | VALID | CAL-401-08
TEST-086 | 2026-08-17T11:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.873 | 120 | 0.426 | 29 | VALID | CAL-401-08
TEST-087 | 2026-08-17T15:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.921 | 120 | 0.406 | 29.8 | VALID | CAL-401-08
TEST-088 | 2026-08-17T19:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.937 | 120 | 0.44 | 27.7 | VALID | CAL-401-08
TEST-088 | 2026-08-17T19:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.937 | 120 | 0.44 | 27.7 | VALID | CAL-401-08
TEST-089 | 2026-08-17T23:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.93 | 120 | 0.452 | 30.1 | VALID | CAL-401-08
TEST-090 | 2026-08-18T03:00:00+08:00 | monitoring | DAY | DP-401A | FT-401 | CV-401 | 62 | 1.936 | 120 | 0.429 | 27.6 | VALID | CAL-401-08
TEST-091 | 2026-08-18T07:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.079 | 120 | 0.109 | 28.2 | VALID | CAL-401-08
TEST-092 | 2026-08-18T11:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.049 | 120 | 0.162 | 27.9 | VALID | CAL-401-08
TEST-093 | 2026-08-18T15:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.075 | 120 | 0.141 | 26.6 | VALID | CAL-401-08
TEST-094 | 2026-08-18T19:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.062 | 120 | 0.185 | 28.3 | VALID | CAL-401-08
TEST-095 | 2026-08-18T23:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.048 | 120 | 0.146 | 27.3 | VALID | CAL-401-08
TEST-096 | 2026-08-19T03:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.046 | 120 | 0.138 | 27.7 | VALID | CAL-401-08
TEST-097 | 2026-08-19T07:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.067 | 120 | 0.121 | 26.5 | VALID | CAL-401-08
TEST-098 | 2026-08-19T11:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.035 | 120 | 0.175 | 28.5 | VALID | CAL-401-08
TEST-099 | 2026-08-19T15:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.071 | 120 | 0.175 | 28.4 | VALID | CAL-401-08
TEST-100 | 2026-08-19T19:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.068 | 120 | 0.157 | 29.3 | VALID | CAL-401-08
TEST-101 | 2026-08-19T23:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.056 | 120 | 0.133 | 26.7 | VALID | CAL-401-08
TEST-102 | 2026-08-20T03:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.068 | 120 | 0.186 | 29.4 | VALID | CAL-401-08
TEST-103 | 2026-08-20T07:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.073 | 120 | 0.122 | 26.8 | VALID | CAL-401-08
TEST-104 | 2026-08-20T11:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.101 | 120 | 0.13 | 27.2 | VALID | CAL-401-08
TEST-105 | 2026-08-20T15:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.032 | 120 | 0.177 | 28.9 | VALID | CAL-401-08
TEST-106 | 2026-08-20T19:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.059 | 120 | 0.184 | 27.8 | VALID | CAL-401-08
TEST-107 | 2026-08-20T23:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.04 | 120 | 0.14 | 27.1 | VALID | CAL-401-08
TEST-108 | 2026-08-21T03:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.051 | 120 | 0.158 | 27.7 | VALID | CAL-401-08
TEST-109 | 2026-08-21T07:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.081 | 120 | 0.17 | 29 | VALID | CAL-401-08
TEST-110 | 2026-08-21T11:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.084 | 120 | 0.192 | 27.6 | VALID | CAL-401-08
TEST-111 | 2026-08-21T15:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.037 | 120 | 0.178 | 27.6 | VALID | CAL-401-08
TEST-112 | 2026-08-21T19:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.05 | 120 | 0.169 | 28.4 | VALID | CAL-401-08
TEST-113 | 2026-08-21T23:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.091 | 120 | 0.131 | 28.9 | VALID | CAL-401-08
TEST-114 | 2026-08-22T03:00:00+08:00 | pilot | DAY | DP-401A | FT-401 | CV-401 | 62 | 2.041 | 120 | 0.175 | 27.1 | VALID | CAL-401-08
TEST-115 | 2026-08-22T07:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.104 | 120 | 0.132 | 28.9 | VALID | CAL-401-08
TEST-116 | 2026-08-22T11:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.096 | 120 | 0.147 | 28.8 | VALID | CAL-401-08
TEST-117 | 2026-08-22T15:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.084 | 120 | 0.159 | 27.9 | VALID | CAL-401-08
TEST-118 | 2026-08-22T19:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.067 | 120 | 0.144 | 27.4 | VALID | CAL-401-08
TEST-119 | 2026-08-22T23:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.075 | 120 | 0.14 | 28.3 | VALID | CAL-401-08
TEST-120 | 2026-08-23T03:00:00+08:00 | pilot | NIGHT | DP-401A | FT-401 | CV-401 | 62 | 2.029 | 120 | 0.147 | 26.6 | VALID | CAL-401-08

## ValidTests
test_id | timestamp_SGT | phase | shift | pump_tag | collected_L | delivery_L_h | strainer_dp_bar
TEST-001 | 2026-08-03T07:00:00+08:00 | baseline | DAY | DP-401A | 2.052 | 61.56 | 0.216
TEST-002 | 2026-08-03T11:00:00+08:00 | baseline | DAY | DP-401A | 2.051 | 61.53 | 0.167
TEST-003 | 2026-08-03T15:00:00+08:00 | baseline | DAY | DP-401A | 2.066 | 61.98 | 0.199
TEST-004 | 2026-08-03T19:00:00+08:00 | baseline | DAY | DP-401A | 2.104 | 63.12 | 0.191
TEST-005 | 2026-08-03T23:00:00+08:00 | baseline | DAY | DP-401A | 2.059 | 61.77 | 0.194
TEST-006 | 2026-08-04T03:00:00+08:00 | baseline | DAY | DP-401A | 2.069 | 62.07 | 0.149
TEST-007 | 2026-08-04T07:00:00+08:00 | baseline | NIGHT | DP-401A | 2.038 | 61.14 | 0.162
TEST-008 | 2026-08-04T11:00:00+08:00 | baseline | NIGHT | DP-401A | 2.045 | 61.35 | 0.165
TEST-009 | 2026-08-04T15:00:00+08:00 | baseline | NIGHT | DP-401A | 2.06 | 61.8 | 0.199
TEST-010 | 2026-08-04T19:00:00+08:00 | baseline | NIGHT | DP-401A | 2.079 | 62.37 | 0.158
TEST-011 | 2026-08-04T23:00:00+08:00 | baseline | NIGHT | DP-401A | 2.092 | 62.76 | 0.186
TEST-012 | 2026-08-05T03:00:00+08:00 | baseline | NIGHT | DP-401A | 2.067 | 62.01 | 0.157
TEST-013 | 2026-08-05T07:00:00+08:00 | baseline | DAY | DP-401A | 2.089 | 62.67 | 0.173
TEST-014 | 2026-08-05T11:00:00+08:00 | baseline | DAY | DP-401A | 2.058 | 61.74 | 0.194
TEST-015 | 2026-08-05T15:00:00+08:00 | baseline | DAY | DP-401A | 2.094 | 62.82 | 0.203
TEST-016 | 2026-08-05T19:00:00+08:00 | baseline | DAY | DP-401A | 2.069 | 62.07 | 0.207
TEST-017 | 2026-08-05T23:00:00+08:00 | baseline | DAY | DP-401A | 2.058 | 61.74 | 0.144
TEST-018 | 2026-08-06T03:00:00+08:00 | baseline | DAY | DP-401A | 2.088 | 62.64 | 0.173
TEST-019 | 2026-08-06T07:00:00+08:00 | baseline | NIGHT | DP-401A | 2.098 | 62.94 | 0.185
TEST-020 | 2026-08-06T11:00:00+08:00 | baseline | NIGHT | DP-401A | 2.054 | 61.62 | 0.186
TEST-021 | 2026-08-06T15:00:00+08:00 | baseline | NIGHT | DP-401A | 2.039 | 61.17 | 0.189
TEST-022 | 2026-08-06T19:00:00+08:00 | baseline | NIGHT | DP-401A | 2.052 | 61.56 | 0.193
TEST-023 | 2026-08-06T23:00:00+08:00 | baseline | NIGHT | DP-401A | 2.101 | 63.03 | 0.188
TEST-024 | 2026-08-07T03:00:00+08:00 | baseline | NIGHT | DP-401A | 2.067 | 62.01 | 0.169
TEST-025 | 2026-08-07T07:00:00+08:00 | baseline | DAY | DP-401A | 2.105 | 63.15 | 0.18
TEST-026 | 2026-08-07T11:00:00+08:00 | baseline | DAY | DP-401A | 2.072 | 62.16 | 0.165
TEST-027 | 2026-08-07T15:00:00+08:00 | baseline | DAY | DP-401A | 2.049 | 61.47 | 0.19
TEST-028 | 2026-08-07T19:00:00+08:00 | baseline | DAY | DP-401A | 2.077 | 62.31 | 0.173
TEST-029 | 2026-08-07T23:00:00+08:00 | baseline | DAY | DP-401A | 2.062 | 61.86 | 0.169
TEST-030 | 2026-08-08T03:00:00+08:00 | baseline | DAY | DP-401A | 2.043 | 61.29 | 0.183
TEST-031 | 2026-08-08T07:00:00+08:00 | baseline | NIGHT | DP-401A | 2.066 | 61.98 | 0.148
TEST-032 | 2026-08-08T11:00:00+08:00 | baseline | NIGHT | DP-401A | 2.084 | 62.52 | 0.195
TEST-033 | 2026-08-08T15:00:00+08:00 | baseline | NIGHT | DP-401A | 2.052 | 61.56 | 0.153
TEST-034 | 2026-08-08T19:00:00+08:00 | baseline | NIGHT | DP-401A | 2.067 | 62.01 | 0.178
TEST-035 | 2026-08-08T23:00:00+08:00 | baseline | NIGHT | DP-401A | 2.037 | 61.11 | 0.17
TEST-036 | 2026-08-09T03:00:00+08:00 | baseline | NIGHT | DP-401A | 2.065 | 61.95 | 0.151
TEST-037 | 2026-08-09T07:00:00+08:00 | baseline | DAY | DP-401A | 2.069 | 62.07 | 0.195
TEST-038 | 2026-08-09T11:00:00+08:00 | baseline | DAY | DP-401A | 2.074 | 62.22 | 0.191
TEST-039 | 2026-08-09T15:00:00+08:00 | baseline | DAY | DP-401A | 2.056 | 61.68 | 0.202
TEST-040 | 2026-08-09T19:00:00+08:00 | baseline | DAY | DP-401A | 2.076 | 62.28 | 0.208
TEST-041 | 2026-08-09T23:00:00+08:00 | baseline | DAY | DP-401A | 2.037 | 61.11 | 0.203
TEST-042 | 2026-08-10T03:00:00+08:00 | baseline | DAY | DP-401A | 2.052 | 61.56 | 0.149
TEST-043 | 2026-08-10T07:00:00+08:00 | baseline | NIGHT | DP-401A | 2.065 | 61.95 | 0.185
TEST-044 | 2026-08-10T11:00:00+08:00 | baseline | NIGHT | DP-401A | 2.038 | 61.14 | 0.198
TEST-045 | 2026-08-10T15:00:00+08:00 | baseline | NIGHT | DP-401A | 2.077 | 62.31 | 0.173
TEST-046 | 2026-08-10T19:00:00+08:00 | baseline | NIGHT | DP-401A | 2.101 | 63.03 | 0.189
TEST-047 | 2026-08-10T23:00:00+08:00 | baseline | NIGHT | DP-401A | 2.043 | 61.29 | 0.189
TEST-048 | 2026-08-11T03:00:00+08:00 | baseline | NIGHT | DP-401A | 2.082 | 62.46 | 0.152
TEST-049 | 2026-08-11T07:00:00+08:00 | baseline | DAY | DP-401A | 2.083 | 62.49 | 0.18
TEST-050 | 2026-08-11T11:00:00+08:00 | baseline | DAY | DP-401A | 2.058 | 61.74 | 0.221
TEST-051 | 2026-08-11T15:00:00+08:00 | baseline | DAY | DP-401A | 2.102 | 63.06 | 0.157
TEST-052 | 2026-08-11T19:00:00+08:00 | baseline | DAY | DP-401A | 2.077 | 62.31 | 0.189
TEST-053 | 2026-08-11T23:00:00+08:00 | baseline | DAY | DP-401A | 2.051 | 61.53 | 0.172
TEST-054 | 2026-08-12T03:00:00+08:00 | baseline | DAY | DP-401A | 2.03 | 60.9 | 0.18
TEST-055 | 2026-08-12T07:00:00+08:00 | baseline | NIGHT | DP-401A | 2.056 | 61.68 | 0.157
TEST-056 | 2026-08-12T11:00:00+08:00 | baseline | NIGHT | DP-401A | 2.063 | 61.89 | 0.19
TEST-057 | 2026-08-12T15:00:00+08:00 | baseline | NIGHT | DP-401A | 2.019 | 60.57 | 0.178
TEST-058 | 2026-08-12T19:00:00+08:00 | baseline | NIGHT | DP-401A | 2.097 | 62.91 | 0.162
TEST-059 | 2026-08-12T23:00:00+08:00 | baseline | NIGHT | DP-401A | 2.088 | 62.64 | 0.181
TEST-060 | 2026-08-13T03:00:00+08:00 | baseline | NIGHT | DP-401A | 2.083 | 62.49 | 0.189
TEST-061 | 2026-08-13T07:00:00+08:00 | monitoring | DAY | DP-401A | 2.084 | 62.52 | 0.188
TEST-062 | 2026-08-13T11:00:00+08:00 | monitoring | DAY | DP-401A | 2.051 | 61.53 | 0.183
TEST-063 | 2026-08-13T15:00:00+08:00 | monitoring | DAY | DP-401A | 2.032 | 60.96 | 0.196
TEST-064 | 2026-08-13T19:00:00+08:00 | monitoring | DAY | DP-401A | 2.039 | 61.17 | 0.196
TEST-065 | 2026-08-13T23:00:00+08:00 | monitoring | DAY | DP-401A | 2.066 | 61.98 | 0.201
TEST-066 | 2026-08-14T03:00:00+08:00 | monitoring | DAY | DP-401A | 2.058 | 61.74 | 0.202
TEST-067 | 2026-08-14T07:00:00+08:00 | monitoring | NIGHT | DP-401A | 2.077 | 62.31 | 0.177
TEST-069 | 2026-08-14T15:00:00+08:00 | monitoring | NIGHT | DP-401A | 2.05 | 61.5 | 0.189
TEST-070 | 2026-08-14T19:00:00+08:00 | monitoring | NIGHT | DP-401A | 2.032 | 60.96 | 0.163
TEST-071 | 2026-08-14T23:00:00+08:00 | monitoring | NIGHT | DP-401A | 2.104 | 63.12 | 0.188
TEST-072 | 2026-08-15T03:00:00+08:00 | monitoring | NIGHT | DP-401A | 2.07 | 62.1 | 0.21
TEST-073 | 2026-08-15T07:00:00+08:00 | monitoring | DAY | DP-401A | 1.929 | 57.87 | 0.434
TEST-074 | 2026-08-15T11:00:00+08:00 | monitoring | DAY | DP-401A | 1.97 | 59.1 | 0.389
TEST-075 | 2026-08-15T15:00:00+08:00 | monitoring | DAY | DP-401A | 1.915 | 57.45 | 0.417
TEST-076 | 2026-08-15T19:00:00+08:00 | monitoring | DAY | DP-401A | 1.927 | 57.81 | 0.398
TEST-077 | 2026-08-15T23:00:00+08:00 | monitoring | DAY | DP-401A | 1.907 | 57.21 | 0.425
TEST-078 | 2026-08-16T03:00:00+08:00 | monitoring | DAY | DP-401A | 1.977 | 59.31 | 0.431
TEST-079 | 2026-08-16T07:00:00+08:00 | monitoring | NIGHT | DP-401A | 1.936 | 58.08 | 0.431
TEST-080 | 2026-08-16T11:00:00+08:00 | monitoring | NIGHT | DP-401A | 1.904 | 57.12 | 0.422
TEST-081 | 2026-08-16T15:00:00+08:00 | monitoring | NIGHT | DP-401A | 1.942 | 58.26 | 0.427
TEST-082 | 2026-08-16T19:00:00+08:00 | monitoring | NIGHT | DP-401A | 1.937 | 58.11 | 0.424
TEST-084 | 2026-08-17T03:00:00+08:00 | monitoring | NIGHT | DP-401A | 1.929 | 57.87 | 0.427
TEST-085 | 2026-08-17T07:00:00+08:00 | monitoring | DAY | DP-401A | 1.943 | 58.29 | 0.404
TEST-086 | 2026-08-17T11:00:00+08:00 | monitoring | DAY | DP-401A | 1.873 | 56.19 | 0.426
TEST-087 | 2026-08-17T15:00:00+08:00 | monitoring | DAY | DP-401A | 1.921 | 57.63 | 0.406
TEST-088 | 2026-08-17T19:00:00+08:00 | monitoring | DAY | DP-401A | 1.937 | 58.11 | 0.44
TEST-089 | 2026-08-17T23:00:00+08:00 | monitoring | DAY | DP-401A | 1.93 | 57.9 | 0.452
TEST-090 | 2026-08-18T03:00:00+08:00 | monitoring | DAY | DP-401A | 1.936 | 58.08 | 0.429
TEST-091 | 2026-08-18T07:00:00+08:00 | pilot | NIGHT | DP-401A | 2.079 | 62.37 | 0.109
TEST-092 | 2026-08-18T11:00:00+08:00 | pilot | NIGHT | DP-401A | 2.049 | 61.47 | 0.162
TEST-093 | 2026-08-18T15:00:00+08:00 | pilot | NIGHT | DP-401A | 2.075 | 62.25 | 0.141
TEST-094 | 2026-08-18T19:00:00+08:00 | pilot | NIGHT | DP-401A | 2.062 | 61.86 | 0.185
TEST-095 | 2026-08-18T23:00:00+08:00 | pilot | NIGHT | DP-401A | 2.048 | 61.44 | 0.146
TEST-096 | 2026-08-19T03:00:00+08:00 | pilot | NIGHT | DP-401A | 2.046 | 61.38 | 0.138
TEST-097 | 2026-08-19T07:00:00+08:00 | pilot | DAY | DP-401A | 2.067 | 62.01 | 0.121
TEST-098 | 2026-08-19T11:00:00+08:00 | pilot | DAY | DP-401A | 2.035 | 61.05 | 0.175
TEST-099 | 2026-08-19T15:00:00+08:00 | pilot | DAY | DP-401A | 2.071 | 62.13 | 0.175
TEST-100 | 2026-08-19T19:00:00+08:00 | pilot | DAY | DP-401A | 2.068 | 62.04 | 0.157
TEST-101 | 2026-08-19T23:00:00+08:00 | pilot | DAY | DP-401A | 2.056 | 61.68 | 0.133
TEST-102 | 2026-08-20T03:00:00+08:00 | pilot | DAY | DP-401A | 2.068 | 62.04 | 0.186
TEST-103 | 2026-08-20T07:00:00+08:00 | pilot | NIGHT | DP-401A | 2.073 | 62.19 | 0.122
TEST-104 | 2026-08-20T11:00:00+08:00 | pilot | NIGHT | DP-401A | 2.101 | 63.03 | 0.13
TEST-105 | 2026-08-20T15:00:00+08:00 | pilot | NIGHT | DP-401A | 2.032 | 60.96 | 0.177
TEST-106 | 2026-08-20T19:00:00+08:00 | pilot | NIGHT | DP-401A | 2.059 | 61.77 | 0.184
TEST-107 | 2026-08-20T23:00:00+08:00 | pilot | NIGHT | DP-401A | 2.04 | 61.2 | 0.14
TEST-108 | 2026-08-21T03:00:00+08:00 | pilot | NIGHT | DP-401A | 2.051 | 61.53 | 0.158
TEST-109 | 2026-08-21T07:00:00+08:00 | pilot | DAY | DP-401A | 2.081 | 62.43 | 0.17
TEST-110 | 2026-08-21T11:00:00+08:00 | pilot | DAY | DP-401A | 2.084 | 62.52 | 0.192
TEST-111 | 2026-08-21T15:00:00+08:00 | pilot | DAY | DP-401A | 2.037 | 61.11 | 0.178
TEST-112 | 2026-08-21T19:00:00+08:00 | pilot | DAY | DP-401A | 2.05 | 61.5 | 0.169
TEST-113 | 2026-08-21T23:00:00+08:00 | pilot | DAY | DP-401A | 2.091 | 62.73 | 0.131
TEST-114 | 2026-08-22T03:00:00+08:00 | pilot | DAY | DP-401A | 2.041 | 61.23 | 0.175
TEST-115 | 2026-08-22T07:00:00+08:00 | pilot | NIGHT | DP-401A | 2.104 | 63.12 | 0.132
TEST-116 | 2026-08-22T11:00:00+08:00 | pilot | NIGHT | DP-401A | 2.096 | 62.88 | 0.147
TEST-117 | 2026-08-22T15:00:00+08:00 | pilot | NIGHT | DP-401A | 2.084 | 62.52 | 0.159
TEST-118 | 2026-08-22T19:00:00+08:00 | pilot | NIGHT | DP-401A | 2.067 | 62.01 | 0.144
TEST-119 | 2026-08-22T23:00:00+08:00 | pilot | NIGHT | DP-401A | 2.075 | 62.25 | 0.14
TEST-120 | 2026-08-23T03:00:00+08:00 | pilot | NIGHT | DP-401A | 2.029 | 60.87 | 0.147

## Evidence
record_id | type | revision | timestamp_or_date | status | content
DOC-401 | DESIGN | 2 | 2026-08-01 | Current | Teaching delivery target62 L/h; band58.9–65.1; fixed command and120s collection.
DOC-401 | DESIGN | 1 | 2026-07-01 | Obsolete | Teaching target60 L/h; superseded byrev2.
CAL-401-08 | INSTRUMENT | 1 | 2026-08-01 | Training evidence | Collection vessel check recorded before baseline; measurement-system adequacy not certified.
EV-401-01 | EVENT | 1 | 2026-08-15T07:00:00+08:00 | Observation | Differential pressure increase and reduced test delivery appear in same period; no cause confirmed.
WO-401-17 | MAINTENANCE | 1 | 2026-08-18T05:00:00+08:00 | Recorded complete | Strainer replaced and verification check performed beforepilot; two changes confound causal attribution.
ACT-401-04 | ACTION | 1 | 2026-08-24 | Open | EngineerR to review removed strainer evidence; no contamination result supplied.

## FMEA_Input
mode_id | function | failure_mode | effect | potential_cause | current_control | evidence | S_provisional | O_provisional | D_provisional | proposed_action | role_owner
FM01 | Meter delivery | Low delivery | Insufficient treatment feed | Restriction hypothesis | Periodic collection test | EV-401-01; TEST-073–090 | 7 | 5 | 4 | Review removed-strainer evidence | Reliability lead
FM02 | Meter delivery | Excess delivery | Excess treatment feed | Wrong setting hypothesis | Setting log review | No occurrence evidence in supplied tests | 7 | 2 | 5 | Review setting change controls | Operations lead
FM03 | Indicate delivery | Misleading reading | Wrong process decision | Instrument or measurement bias | Vessel verification record | CAL-401-08; adequacy not established | 6 | 3 | 6 | Perform approved measurement-system review | Instrumentation lead
FM04 | Maintain containment | External leakage | Exposure and loss of containment | Seal deterioration hypothesis | Visual inspection | No leak event supplied; prospective scenario | 9 | 2 | 5 | Review compatibility and inspection evidence | Safety reviewer
FM05 | Collect comparable tests | Invalid test duration | Biased apparent delivery | Timing error | Duration field and quality flag | TEST-083 | 4 | 4 | 3 | Review timing and data-validation controls | Quality lead
FM06 | Retain accurate records | Duplicate event | Biased counts and statistics | Export duplication | Event-key uniqueness check | Duplicate TEST-088 | 4 | 4 | 2 | Validate ingestion deduplication ledger | Data owner

## WeeklyEvents
week | phase | test_opportunities | deviations | definition
W01 | baseline | 168 | 14 | Logged collection-test acceptance deviations; no exposure-severity inference
W02 | baseline | 168 | 16 | Logged collection-test acceptance deviations; no exposure-severity inference
W03 | baseline | 168 | 13 | Logged collection-test acceptance deviations; no exposure-severity inference
W04 | baseline | 168 | 18 | Logged collection-test acceptance deviations; no exposure-severity inference
W05 | baseline | 168 | 15 | Logged collection-test acceptance deviations; no exposure-severity inference
W06 | baseline | 168 | 17 | Logged collection-test acceptance deviations; no exposure-severity inference
W07 | pilot | 168 | 6 | Logged collection-test acceptance deviations; no exposure-severity inference
W08 | pilot | 168 | 5 | Logged collection-test acceptance deviations; no exposure-severity inference

## DefectCounts
category | baseline_count | evidence_status
Low delivery | 55 | Observed category; mechanism unconfirmed
Test validity | 16 | Administrative/test issue
Missing evidence | 12 | Incomplete record
Other | 10 | Needs classification review

## Parameters
parameter | value | unit_or_note
duration_s | 120 | Standard collection duration; fictional
target | 62 | L/h
LSL | 58.9 | L/h
USL | 65.1 | L/h
d2 | 1.128 | MR of two; NIST individuals-chart estimator
baseline_n | 60 | Baseline tests only

## ScoringNote
Provisional rating definitions
# Provisional workshop scoring Original synthetic IES training case. Fictional assets, people, observations and engineering requirements. No real operating limits or work authorisation. Pending alignment to the user-supplied Excel prompts. S/O/D are supplied workshop judgements, not values estimated from the small test dataset. S:1 negligible impact,4 local rework,6 degraded process decision,7 treatment-process impact requiring review,9 potential serious exposure. O:1 remote,2 low,3 occasional,4 recurring administrative/test issue,5 repeatedly observed condition. D:1 near-certain pre-effect detection through validated controls,2 high detectability,3 likely detection,4 periodic test may detect,5 incomplete assurance,6 weak detection assurance. Larger D means poorer detectability. Other values need a documented agreed definition before use. RPN is a teaching prioritisation aid, not a safety acceptance criterion. Severity9 receives review regardless of rank. Do not reduce residual scores for an action that is merely proposed.
Severity gate | S>=9 requires explicit review regardless of RPN.

## Prompts
prompt_id | purpose | prompt
SPC1 | Audit the source | Using RawTests, audit test_id uniqueness, missing collected_L, duration_s and quality_flag. Do not modify RawTests. Create a QualityAudit table with record ID, issue, inclusion decision and reason. Use one unique record per test, require VALID and 120 seconds, and never discard an excursion solely because it is extreme. Report raw, unique and valid counts.
SPC2 | Calculate the baseline | Use ValidTests in time order. In Analysis create delivery_L_h = collected_L*3600/120. Use only the 60 baseline records to calculate mean and successive moving ranges; do not bridge across phases. Estimate sigma = MRbar/1.128 and individuals limits mean +/-3*sigma. Put constants and specifications in Parameters and show formulas, units and referenced rows.
SPC3 | Plot and interpret | Create an Excel line chart of delivery_L_h by timestamp for baseline, monitoring and pilot, with the fixed baseline mean/UCL/LCL. Flag points outside the limits without refitting them. Report phase counts and affected IDs. Explain the monitoring shift as a signal requiring investigation, not a proven restriction diagnosis. Keep invalid and missing tests visible in QualityAudit.
SPC4 | Check capability | Using fictional test specifications 58.9–65.1 L/h, calculate baseline Cp and Cpk from the stated within-process estimator. State assumptions: stable baseline, adequate measurement, suitable distribution and independence. Do not use a good Cp to claim the later monitoring period is stable. Review potential shift/measurement effects and compare with Worked-Reference.xlsx.
FMEA1 | Structure the review | Use FMEA_Input and Evidence. Create FMEA_Review with function, mode, effect, potential cause, current control, evidence, supplied provisional S/O/D, RPN, action, owner and status. Keep the six mode IDs. Separate actual observations from prospective scenarios. Use ScoringNote for definitions and do not infer occurrence ratings from the short test series.
FMEA2 | Calculate and prioritise | Add an Excel formula RPN=S*O*D for every row. Sort a view by RPN descending while preserving mode IDs and source rows. Add a separate high-severity review flag for S>=9. Create an RPN column chart. Do not treat rank or low RPN as evidence of safety acceptance.
FMEA3 | Challenge with personas | Simulate reliability, operations and safety review lenses. First return one separate evidence-based concern per role. Run two concise challenge/response rounds, citing mode IDs and evidence records. A moderator returns agreed revisions, unresolved disagreement and missing evidence. Do not force consensus or invent approval. Keep residual ratings unassessed until action-effectiveness evidence exists.
DMAIC1 | Define and measure | Use WeeklyEvents, DefectCounts and Evidence. Draft a DMAIC table in Excel: phase, claim, metric, source, limitation, next action. Define the CTQ as delivery-test acceptance deviation, not chemical compliance. Calculate baseline and pilot rates using summed deviations divided by summed opportunities, not a simple average when denominators differ.
DMAIC2 | Analyse | Create a Pareto table and chart from baseline DefectCounts, including cumulative percentage. Reconcile the total with baseline WeeklyEvents. Compare the phase rates and express both percentage-point and relative change. Explain that fewer deviations after two concurrent changes do not isolate the cause or establish sustained improvement.
DMAIC3 | Improve and control | Draft a controlled follow-up trial and ControlPlan table: metric, source, frequency, owner, signal rule, review response and evidence. Link to SPC signals and FMEA actions. Preserve the open removed-strainer review. Do not claim causal proof, savings or operational approval not supported by the source. End with a six-cell management summary and unresolved questions.

## QualityAudit
test_id | issue | decision | reason

## Analysis
test_id | timestamp | phase | shift | pump | collected_L | delivery_L_h | strainer_dp_bar | MR_baseline | centre | UCL | LCL | signal

## SPC_Summary
metric | result | units_or_interpretation

## FMEA_Review
mode_id | failure_mode | S | O | D | RPN | severity_gate | action | owner | residual_status

## DMAIC
phase | claim | source | limitation | next_action

## ControlPlan
metric | source | frequency | owner | signal_rule | review_response

## Evaluation
prompt_id | tool_action | source_check | formula_check | correction | review_minutes